## Slide 1: Weather Monitoring System

## Slide 2: User Requirements
Design a weather monitoring system that detects the following parameters
  Temperature
  Pressure
  Relative humidity
  Wind Speed
  Wind Direction
  Rainfall
  Solar Radiation
This information is sent to a remote system every 5 minutes

## Slide 3: All parameters sensed - every minute

## Slide 4
Every 5 minutes – data collected
Averaged & sent to Central computer

## Slide 5
Communication is Serial
Wired
RS232C in null Modem
Communication Speed is 9600 Baud

## Slide 6: Temperature
Range: - 20° C to + 50° C
Resolution - 1° C

## Slide 7: Wind Speed
Range: 0-100 MPH
Resolution: 0.5 MPH

## Slide 8: Wind Direction
Range: 0 to 360°
Resolution: 2o

## Slide 9: Pressure
Range: 800-1100 millibars
Resolution: 2 millibars

## Slide 10: Humidity- Relative Humidity
Range: 0 -100%
Resolution: 1%

## Slide 11: Solar Radiation
Range: 0 -1500W/m2
Resolution: 10W/m2

## Slide 12: Rainfall
Range: 0 -20 mm/min
Resolution: 0.1mm /min

## Slide 13: Weather Monitoring System
Step 1 of the Design

## Slide 14: Where to start ?

## Slide 15: Sensors
Analog Output
  Varying Current
  Varying Voltage
Serial Digital output
Pulses/ Second

## Slide 16: Temperature Sensor
System Specifications
Range: - 20° C to +50° C
Resolution: - 1° C
WE 700
Output: 4-20mA
Range: -50° C to + 50° C
Resolution: 2° F or 1° C
Operating Voltage: 10-36VDC
Warm Up Time: 5 seconds minimum
Operating Temperature: -50°C to +100°C

## Slide 17: Wind Speed Sensor
Sensor Specifications
Range: 0-100 MPH
Resolution: 0.5 MPH
WE 550
Output: 4-20mA
0-100 MPH
Resolution: .5 MPH over the range 11 to 55 MPH
Operating Voltage: 10-36VDC
Warm Up Time: 3 seconds minimum
Operating Temp: -40° to +55°C

## Slide 18: Wind Direction Sensor
Sensor Specifications
Range: 0 to 360°
Resolution: 2o
WE570
Output 4-20 mA
Range 0 to 360°
Sensitivity 1 m/s (2.2 mph)
Resolution 1% full scale
Operating Voltage 10 to 36 VDC
Warm-up Time 3 seconds minimum
Operating Temperature:-40° to +55°C

## Slide 19: Barometric Pressure Sensor
System Specification
Range: 800-1100 millibars
Resolution: 2 millibars
WE 100
Output: 4-20mA
Range: 800-1100 millibars
Resolution: 0.5% of full scale
Operating Voltage: 10-36VDC
Warm Up Time: 3 seconds minimum
Operating Temp: -40° to +55°C ,

## Slide 20: Relative Humidity
System Specifications
Range: 0 -100%
Resolution: 1%
WE 600
Output: 4-20mA
Range: 0-100% RH
Resolution: + 0.5% RH
Operating Voltage: 10-36VDC
Current Draw: 3 mA plus sensor
Warm Up Time: 3 seconds minimum
Operating Temp: -40° to +55°C

## Slide 21: Solar Radiation Sensor
Sensor Specifications
Range: 0 -1500W/m2
Resolution: 10W/m2
WE 300
Output: 4-20mA
Range: 0-1500 W /m2
Resolution: 1% of full scale
Operating Voltage: 10-36VDC
Warm Up Time: 3 seconds minimum
Operating Temperature: -40°C to +55°C.

## Slide 22: Rainfall
System Specifications
Range: 0 -20 mm/min
Resolution: 0.1mm /min
Lambrecht – Precipitation sensor
Output: 4-20mA
Range: 0-25 mm/m
Resolution: 0.1mm/min
Operating Voltage: 10-36VDC
Current Draw: 3 mA plus sensor
Warm Up Time: 3 seconds minimum
Operating Temp: -40° to +55°C

## Slide 23: Output
System Specifications
Communication is Serial
Wired
RS232C in null Modem
Communication Speed is 9600 Baud
16550

## Slide 24: Timing
System Specifications
Every 5 minutes – data collected
Every 1 Minute – Data Sensed
8253/8259

## Slide 25: Weather Monitoring System
Step 2 Interfacing the sensor

## Slide 26: Step 2 : How to interface Sensor to system
Analog Current 4 -20 mA
Generally Measure Voltage
Current to Voltage Conversion ??

## Slide 27: Current to Voltage Conversion
1.25
6.25
0V
5V

## Slide 28: Analog to Digital
7 Analog outputs from 0-5V
Size of ADC
  Resolution of sensor
  19.6mv ( 8-bit ADC)
  (5.0 – 0.0 )V/256

## Slide 29: Sensor Resolution Vs ADC Resolutions
Temperature Sensor
Range: - 20° C to +50° C
Resolution: - 1° C
70
5/70
71.4 mV
ADC
256
19.6 mV

## Slide 30: Sensor Resolution Vs ADC Resolutions
Wind Speed Sensor
Range: 0-100 MPH
Resolution: 0.5 MPH
200
5.0/ 200
25mV
ADC
256
19.6 mV

## Slide 31: Sensor Resolution Vs ADC Resolutions
Wind Direction Sensor
Range: 0 to 360°
Resolution: 2o
180
5.0/ 180
27.78mV
ADC
256
19.6 mV

## Slide 32: Sensor Resolution Vs ADC Resolutions
Pressure Sensor
Range: 800-1100 millibars
Resolution: 2 millibars
150
5.0/ 150
33.3mV
ADC
256
19.6 mV

## Slide 33: Sensor Resolution Vs ADC Resolutions
Relative Humidity Sensor
Range: 0 -100%
Resolution: 1%
100
5.0/ 100
50mV
ADC
256
19.6 mV

## Slide 34: Sensor Resolution Vs ADC Resolutions
Solar Radiation Sensor
Range: 0 -1500W/m2
Resolution: 10W/m2
150
5.0/ 100
50mV
ADC
256
19.6 mV

## Slide 35: Sensor Resolution Vs ADC Resolutions
Rainfall Sensor
Range: 0 -20 mm/min
Resolution: 0.1mm /min
200
5.0/ 200
25mV
ADC
256
19.6 mV

## Slide 36: Step 2 : How to interface Sensor to system
No of analog i/ps-7
8-channel ADC
8-bit
0808 – 8 channel, 8-bit ADC

## Slide 37
ADC 0808
IN0 IN1 IN2 IN3 IN4 IN5 IN6 IN7
Analog
I/ps
CLK
DB0 –DB7
AD0
AD1
AD2
VREF+
VREF-
5V
0V
Vcc
GND
Supply
EOC
SOC
ALE
OE
5 V = 19.6078 mV
255

## Slide 38: Interface the ADC

## Slide 39: How to interface ADC to 8086 ?
2 ports available use it for ADC

## Slide 40
ADC 0808
IN0 IN1 IN2 IN3 IN4 IN5 IN6 IN7
sensors
1 MHz
CLK
DB0 –DB7
PB0 –PB7
AD0
AD1
AD2
PC0 PC1 PC2
VREF+
VREF-
5V
0V
Vcc
GND
Supply
EOC
INTR
SOC
ALE
OE
PC3
PC4
PC5

## Slide 41: Generate 1 MHz
Use 8254
Any other timing
Read every 1 Minute

## Slide 42: STEP 3 : 1 MHz clock & 5 MIN Interrupt
Use 8254

## Slide 43
CLK0
GATE0
OUT0
5 MHz
5V
OUT1
GATE1
CLK1
1 MHz
Count = 5d
mode3
mode2
CLK2
GATE2
OUT2
5V
1 minute
Count =6000d
mode2
ADC CLK
5 MHz
Count = 50000d
5V
100 Hz
TIMER INT

## Slide 44: STEP 4: Interrupt Generation
Use 8259

## Slide 45
8259
IR0
INT
INTA
CAS0 CAS1 CAS2
SP/EN
5V
IR1
Timer
ADC

## Slide 46: Step 5: Output Interface
Serial Port Null Modem
 | 16550 | 
 |  | DTR
RTS |  | DSR
CTS |  | DCD
RXD |  | 
TXD |  | 

## Slide 47: STEP 6: How to interface 8255, 8254 & 8259,16550
Memory mapped/ IO mapped ?
Fixed/ Variable addressing ?
Address
80 - 86H -8255
90H - 96H – 8254
A0H – A2H - 8259
B0H - BEH - 16550
Incremental Addressing

## Slide 48
LS138
A0
G2A G1
G2B
I2 I1 I0
A6 A5 A4
O1
8254
O0
O2
8255
8259
M/IO’
A7
16550
O3

## Slide 49: STEP 7: HOW to Interface Memory
How much memory ?
ROM/RAM?
RAM – minimum 2k chip- 4k
ROM – minimum 2k chip – 4k + 4k
ROM1 00000H
ROM2 FF000H
RAM 01000H

## Slide 50
LS138
GND
G2A G1
GND
G2B
I2 I1 I0
A16 A13 A12
O1
RAM
O0
O7
ROM1
ROM2
M/IO’
A0
WR’
BHE’
WR’
WRL’
WRH’
Memory Decoder

## Slide 51
Interface to the processor
8255
A0
A1
A1
A2
CS
RD
WR
RD
WR
D0 – D7
D0 – D7
RESET
RESET from 8284

## Slide 52
8086
A16-A19 S6-S3
BHE’/S7
LS373
G
ALE
LS373
G
LS373
G
AD8-AD15
AD0-AD7
OE’
OE’
OE’
A16-A19
BHE’
A8-A15
A0-A7
MN/MX’
5V
System Bus of 8086 (Address)

## Slide 53
8086
AD8-AD15
AD0-AD7
MN/MX’
5V
LS245
DIR
LS245
OE’
OE’
DIR
DT/R’
DEN’
D8-D15
D0-D7
RD
WR
IO/M
MEMR
MEMW
IOR
IOW
LOGIC
CIRCUIT
LS244
OE’
System Bus of 8086(Data + Control)
next

## Slide 55
CLK
RESET
MN/MX
READY
VCC
GND
HOLD
NMI
5 V
8284
15 M Hz
8086 Inputs

## Slide 56
Step 8: Software
Main
Branch to end
of IVT
Initialize 8255,
8254,8259
A
A
Start Conversion
for sensor
Wait for
Int
All
sensors
read
Y
N
B
B
16550 send data
Wait for
5 min INT
ISR1
IRET
SOC (S1-S6)
ISR2
IRET
Read ADC

## Slide 57
Step 8: Software - ISR
ISR 1
A
Start Conversion
for sensor
All
sensors
read
Y
N
Send via 16550
ISR2
IRET
Read ADC
Wait for
Int
Enable INT
A
IRET

## Slide 58: Initializing 8255
i8255: mov al,10000010b
out 86H , al

## Slide 59: Initializing 8254
i8254: mov al,00110110b
out 8EH , al
mov al,01110101b
out 8EH , al
mov al,10110101b
out 8EH ,al

## Slide 60: Initializing 8254
mov al,5
out 88H , al
mov al,0
out 88H , al
mov al,50h
out 8AH , al
mov al,0C3h
out 8AH , al
mov al,30h
out 8CH ,al
mov al,75h
out 8CH , al

## Slide 61: Initialising 8259
I8259: mov al,1111 1100b
out 90h,al
mov al,1000 0000b
out 92h,al
mov al,0000 0011b
out 92h,al
mov al,1111 1100b
out 92h,al

## Slide 62: 16550 Initialization
9600 baud
8 data
Odd parity
1 stop
SA – F0H

## Slide 63: 16550 initialization
LINE EQU 0A6H
LSB EQU 0A0H
MSB EQU 0A2H
FIFO EQU 0A4H
INIT:
  MOV AL,10001011B
  OUT LINE,AL
  MOV AL,120
  OUT LSB,AL
  MOV AL,0
  OUT MSB,AL
  MOV AL,00001011B
  OUT LINE,AL